## Sheet1
TagNo | Item Name | Quantity | Project | Plate MATERIAL | Flange MATERIAL | Flange Type | Piece Type | Weld Type | Holder Type | Line_Size | Size in NPS OR DN | Flange Schedule | Pipe Wall Thk | Rating | RJ HOLDER MATERIAL | Drain/Vent | Smooth Finish | Serration | Stellite | Fluid/Service_Name | Service Discription | Service Type | Calculation Standard | Flow Element Type | Flow Rate Unit | Flow Rate Minimum | Flow Rate Maximum | Flow Rate Normal | Flow Rate at FullScale | Tapping | Multi Hole | Pipe Material | Pressure Unit | Temp Unit | Viscosity Unit | Density Unit | Density_Calc_Method | MolecularWeight_Customer | Compressibilty_atFlow_Customer | Compressibilty_atBase_Customer | Gas Name | Base Pressure | Upstream Pressure | Base_Temperature | Operating_Temperature | Vapour_Pressure | Density_at_Base_Customer | Density_at_Flow_Customer | Viscosity_Customer | IsentropicExponenet_Customer | DP Unit | DP at Full Scale | Design Pressure Discription | Design Pressure | Design Temp Discription | Design Temp | Flange Standard | Plate Thk Customer | Spare Plate Required | Stud/Nut | Gasket | JackBolt | Packing_Cost_Manual | Accessories | Accessories_Amt | IBR | IBR_Amt_Manual | Nace | Nace_Type | Nace_Percent | Calibration | CalibrationAmt_Manual | Freight_Required | Freight_Amt_Manual | Special_Requirement | Special_Requirement_Amt | OFA Tap Orientation | FNA Tap Orientation | Venturi Tap Orientation | Plug_Material | Pressure_Tap_Angle | JackBolt_Position | ItemCode_Heading | ItemCode | TestSchedule | FNA Pipe Machining Required | FNA Pipe Machined Cost | FNA Total Assy. Length | FNA Upstream Length | FNA Pipe Length Show to Customer | FNA Pipe Length Customer | Chamfer | ØD1 | Adapter Rating | Flow Nozzle Holding Ring Material | Flow Nozzle Material | Nipple Material | Nipple Size | Nipple Schedule | Nipple Quantity | Venturi Throat Material | Cyllinder Material | Cone Material | Piezometer Ring Material | End Flange Standard | End Flange Type | End Flange Material | End Flange Rating | No of End Flange | Adapter Material | No. of Tapping 1 | Tap Size 1 | No. of Tapping 2 | Tap Size 2 | Companion Flange Required | Tapping Flange | Tapping Flange Size | PitotTube Type | Duct Inside Width | Duct Outside Width | Duct Inside Height | Duct Outside Height | PitotTube Probe Material | Pitot Tube Type | Pitot End Support | Clamping Condition | Pitot Tube End Connection Material | Pitot Tube Sleeve Material | tag_number
303-FE-0701 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.1 | WNRF |  |  |  | 6 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG TO BOTTLING PLANT | LPG TO BOTTLING PLANT | LIQUID | ISO5167 | Concentric: Flange Taps | Kg/h | 12978 | 51560 | 43310 | 67028 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 36.5 | Design Temp. | -45 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0702 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.2 | WNRF |  |  |  | 8 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG TNSFR PMP FR NEW BLT -303-P-312 O/T | LPG TNSFR PMP FR NEW BLT -303-P-312 O/T | LIQUID | ISO5168 | Concentric: Flange Taps | Kg/h | 33733 | 85074 | 70895 | 110597 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 34 | Design Temp. | -45 to 65 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0703 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.3 | WNRF |  |  |  | 8 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG TNSFR PMPS-BTL PLNT 303-P-311 O/T | LPG TNSFR PMPS-BTL PLNT 303-P-311 O/T | LIQUID | ISO5169 | Concentric: Flange Taps | Kg/h | 33733 | 85074 | 70895 | 110597 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 34 | Design Temp. | -45 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0704 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.4 | WNRF |  |  |  | 8 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG TNSFR PMPS-BTL PLNT 303-P-311 O/T | LPG TNSFR PMPS-BTL PLNT 303-P-311 O/T | LIQUID | ISO5170 | Concentric: Flange Taps | Kg/h | 33733 | 85074 | 70895 | 110597 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 34 | Design Temp. | -45 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0705 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.5 | WNRF |  |  |  | 6 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG FROM FROM 303-P-317A/B | LPG FROM FROM 303-P-317A/B | LIQUID | ISO5171 | Concentric: Flange Taps | Kg/h |  | 51560 | 43310 | 67028 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 36.5 | Design Temp. | -45 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0708 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.6 | WNRF |  |  |  | 8 | INCH | Standard |  | 300 |  | VENT |  |  |  | LPG FROM 303-P-311/312/316 | LPG FROM 303-P-311/312/316 | LIQUID | ISO5172 | Concentric: Flange Taps | Kg/h |  | 85074 | 70895 | 110597 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 515.6 | [6 empty] | 42 | 10.92 | 553 |  | 0.11 |  | mm WC,4°C | 2500 | Design Pressure | 34 | Design Temp. | -45 to 65 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-0801 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A350 GR. LF2 CL.7 | WNRF |  |  |  | 6 | INCH | Standard |  | 300 |  | VENT |  |  |  | PROPYLENE FRM 303-P314/315 | PROPYLENE FRM 303-P314/315 | LIQUID | ISO5173 | Concentric: Flange Taps | Kg/h | 12741 | 36270 | 30225 | 47151 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 465 | [6 empty] | 46.4 | 19.47 | 523 |  | 0.08 |  | mm WC,4°C | 2500 | Design Pressure | 36.5 | Design Temp. | -45 |  |  |  | A320 Gr.L7 / A194 Gr.4 | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A320 Gr.L7 / A194 Gr.4 | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE -1010 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 2 | INCH | XS |  | 300 |  | DRAIN |  |  |  | FUEL GAS TO FLARE HEADER | FUEL GAS TO FLARE HEADER | GAS | ISO5174 | Concentric: Flange Taps | Kg/h | 44 | 44 | 44 | 70 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 15.4 | 0.992 | [5 empty] | 40 | 0.012 | 2.645 |  | 0.012 | 1.188 | mm WC,4°C | 2500 | Design Pressure | 7 | Design Temp. | 75 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-1011 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 4 | INCH | Standard |  | 300 |  | DRAIN |  |  |  | NITROGEN TO USERS | NITROGEN TO USERS | GAS | ISO5175 | Concentric: Flange Taps | Nm3/h | 41.8 | 641.8 | 5.5 | 835 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 28 | 0.998 |  |  | 1.033 |  | 0 | 40 | 0.0198 | 9.41 |  | 0.0198 | 1.41 | mm WC | 2500 | Design Pressure | 11 | Design Temp. | 65 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE -1016 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 2 | INCH | XS |  | 300 |  | VENT |  |  |  | FROM OWS PIT | FROM OWS PIT | LIQUID | ISO5176 | Concentric: Flange Taps | Kg/h |  | 3267 | 2970 | 4248 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  |  | 0.078 | [5 empty] | 45 |  | 1015 |  | 225.5 |  | mm WC,4°C | 2500 | Design Pressure | 10 | Design Temp. | 65 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE -1017 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 4 | INCH | Standard |  | 300 |  | VENT |  |  |  | CRWS FROM CRWS PIT PMP | CRWS FROM CRWS PIT PMP | LIQUID | ISO5177 | Concentric: Flange Taps | Kg/h | 33165 | 36630 | 33165 | 47619 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 990 | 0.078 | [5 empty] | 45 | 0.078 | 1015 | 990 | 0.59 |  | mm WC,4°C | 2500 | Design Pressure | 10 | Design Temp. | 65 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-1101 | Orifice Flange Assy. | 1 |  | SS316 | A182GR.F316 | WNRF |  |  |  | 3 | INCH | 10S |  | 300 |  | DRAIN |  |  |  | INSTRUMENT AIR | INSTRUMENT AIR | GAS | ISO5178 | Concentric: Flange Taps | Nm3/h | 119.9 | 119.9 | 119.9 | 180 | Flange |  | SS316 | kgf/m2(g) | °C | cP | kg/m3 |  | 28.9 | 0.997 |  |  | 1.033 |  | 0 | 40 |  | 8.23 |  | 0.0199 | 1.42 | mm WC,4°C | 2500 | [7 empty] | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-1102 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 4 | INCH | Standard |  | 300 |  | VENT |  |  |  | SW TO UTILITY STATIONS | SW TO UTILITY STATIONS | LIQUID | ISO5179 | Concentric: Flange Taps | Kg/h | 10000 | 10000 | 10000 | 15000 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 994 | 0.04 | [5 empty] | 35 | 0.04 | 1015 | 994 | 0.719 |  | mm WC,4°C | 2500 | Design Pressure | 13.2 | Design Temp. | 65 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-1103 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 3 | INCH | Standard |  | 300 |  | DRAIN |  |  |  | PLANT AIR TO UTILITY STATIONS | PLANT AIR TO UTILITY STATIONS | GAS | ISO5180 | Concentric: Flange Taps | Nm3/h | 200 | 200 | 200 | 300 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 28.9 | 0.997 |  |  | 1.033 |  | 0 | 40 | 0.019 | 8.23 |  | 0.019 | 1.42 | mm WC,4°C | 2500 | Design Pressure | 7 | Design Temp. | 65 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE-1104 | Orifice Flange Assy. | 1 |  | MONEL 400 | ASTM A105 (HOT DIP GALVANIZED) | WNRF |  |  |  | 3 | INCH | Standard |  | 300 |  | DRAIN |  |  |  | DW TO UTILITY STATIONS | DW TO UTILITY STATIONS | LIQUID | ISO5181 | Concentric: Flange Taps | Kg/h | 10000 | 10000 | 10000 | 15000 | Flange |  | Carbon Steel | kgf/m2(g) | °C | cP | kg/m3 |  | 994 | 0.07 | [5 empty] | 46 | 0.07 | 1015 | 994 | 0.72 |  | mm WC,4°C | 2500 | Design Pressure | 7 | Design Temp. | 65 |  |  |  | A193 Gr B7 (HOT DIP GALVANIZED) / A 194 Gr 2H (HOT DIP GALVANIZED) | MONEL Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
303-FE -1105 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A105N | WNRF |  |  |  | 3 | INCH | Standard |  | 300 |  | VENT |  |  |  | LP STEAM TO UTILITY STATIONS | LP STEAM TO UTILITY STATIONS | VAPOUR (STEAM) | ISO5182 | Concentric: Flange Taps | Kg/h | 600 | 600 | 600 | 900 | Flange |  | Carbon Steel | kgf/cm2(g) | °C | cP | kg/m3 |  | 18 | 0.988 | [5 empty] | 180 | 0.015 | 2.189 |  | 0.015 | 1.34 | mm WC,4°C | 2500 | Design Pressure | 7 | Design Temp. | 320 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & SS 316 Inner & C.S. Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
374-FE-0201 | Orifice Flange Assy. | 1 |  | SS316 | ASTM A182 F304 | WNRF |  |  |  | 4 | INCH | 10S |  | 300 | [5 empty] | DM WTR TO 374-T-303/304 | DM WTR TO 374-T-303/304 | LIQUID | ISO5183 | Concentric: Flange Taps | Am3/h | 50 | 53 | 53 | 70 | Flange |  | SS304 | kgf/cm2(g) | °C | cP | kg/m3 |  |  | 0.055 |  |  | 1.033 |  | 0 | 40 |  | 1015 | 1000 | 0.651 |  | mm WC,4°C | 2500 | Design Pressure | 11 | Design Temp. | 5 |  |  |  | A193 Gr.B7 / A194 Gr.2H | SS 316 Spiral Wound with Graphite Filler & C.S Outer Ring | A193 Gr.B7 / A194 Gr.2H | [14 empty] | 45 & 135 | [33 empty] | 2 Pairs | 1/2" NPT(F)
073-FE-1301 | [128 empty] | 073-FE-1301
073-FE-1302 | [128 empty] | 073-FE-1302
073-FE-1303 | [128 empty] | 073-FE-1303
073-FE-1304 | [128 empty] | 073-FE-1304
073-FE-1305 | [128 empty] | 073-FE-1305